## Slide 1
03/05/2016
Automation Fieldbuses
Practical examples

## Slide 2
0 – who we are …
1 – Aveiro Harbour
Needs
Solutions
Simple and scalable
2 – Fieldbus in CUF
Why
How
Time management in FF
Anatomy of a FF device
Hacking with FF
3 – Remote internet access to a smart FIELD device
ET phone home …
INDEX

## Slide 3
0 – Who we are
José de Mello, SGPS
BRISA
Mobility, infrastructures and highways
CUF
Chemical industry and nanostructed materials
JOSÉ DE MELLO SAÚDE
Private health facilities and public-private partnerships
MONTE DE RAVASQUEIRA
Wine production and commercialization
JOSÉ DE MELLO RESIDENCIAIS E SERVIÇOS
Residential solutions for seniors and rehabilitation programs
MGI CAPITAL sgps,sa
Industrial maintenance and photovoltaic parks

## Slide 4
1 – Gafanha da Nazaré, Harbour

## Slide 5
1 – Gafanha da Nazaré, Harbour
Client’s needs …
Tank Stock levels
Security cameras

## Slide 6
1 – Gafanha da Nazaré, Harbour
Proposed solution
MODBUS TCP
Ethernet card
+
modbus driver
Line of sight 200m
Multiple 4-20 mA signals
Switch 24 ports Gigabit c/VLAN & POE
PLC Schneider STB Modbus TCP (Remote IO, no logic required
Omni Antenna
Directional Antenna

## Slide 7
1 – Gafanha da Nazaré, Harbour
Traffic management
VLAN 1 – Video TCP Data
VLAN 2 – Modbus TCP Data
MB/s of data (millions of bytes per sec)
B/s of data (some bytes per sec)
Continuous data flow
Every couple of seconds
Fast protocol
Modbus is a slow protocol, either RTU or TCP. But speed is not an issue in this case
VLAN limited to 80% bandwidth
VLAN not limited. Does it require 20% bandwidth ? No

## Slide 8
1 – Gafanha da Nazaré, Harbour
Simple and scalable
Future Loading Docks
Security cameras

## Slide 9
2 – Fieldbus in CUF
Why ?
Stick with 4-20 mA
  Pre-made engineering
  Well know problems
  Standard
  Engineering companies lobby heavilly in favor of 4-20mA
Evolve to a digital protocol
  Promises of:
    Less cabling
    Reliable signals
    Equipment diagnostics
    Configuration and flexibility over field devices
  Engineering and startup a lot more complex

## Slide 10
Fieldbus in CUF
In 2007 there were not that may choices available.
Chose Foundation Fieldbus (FF)
Has some features that exist in the analog world (4-20mA) and adds some additional benefits.
Similarities
- Loop integrity
- Standard cabling
- Bus powered instruments
- Fitted for Intrinsic Safety (IS) electrical certification
Additional Benefits
  1- More functionalities by using digital communications
  2- Less cabling – several devices on the same pair.
  3- A lot less connections in the IO cabinets.
  4- The field instruments behave like devices on the control network, with online diagnostic.

## Slide 11
Fieldbus in CUF
How – the hard part
1 Fieldbus Foundation Cabinet
2 redundant cards per base
4 segments per base
2 power conditioners per segment
2 power supplies per base
Total :
  38 segments / cables
  276 devices

## Slide 12
Fieldbus in CUF
FF

## Slide 13
Hardware
600
1200

## Slide 14
Hardware

## Slide 15
Hardware – Types of field boxes
Ex d Device
Ex ia Device
High Current
“High Current”
“Low Current”
Does not get enough current to generate a spark
Classified zone (ATEX zone 0/1/2)
Fewer instruments per box
Shorter distance to the device
More expensive solution
Fire is contained within the body
Unclassified zone
High current up to the device
Allows bigger distances
Isolated instruments, one output does not affect the others
Segment Protector (SP)
Field Barrier (FB)

## Slide 16
Hardware

## Slide 17
Software
Getting things to work
Printers on a network
need specific drivers to work
Fieldbus devices on a segment
need specific drivers to work
Must match brand, model and revision

## Slide 18
Software
Device drivers
FDT tecnology – DD – Device Descriptors
Text files that describe with a pre-defined syntax the characteristics and capabilities of the devices
DTM – Device Type Manager
Compiled DLL that can be installed on the host and provides graphical access to the inner workings of the device

## Slide 19
Software
DTM Files
Work
Provide DTM’s
Some Models
Some brands
FF Devices

## Slide 20
Software
Time Management in a FF segment
Free time for other operations
Uploads, Downloads, alarms, additional variables besides the official ones.

## Slide 21
Software
Anatomy of a FF Device
1 per measurment sensor
CPU
1 per variable

## Slide 22
Software
Transmitters & Sensors
FF CPU’s (transmitters) at
the ground flour level
FF Sensors scatered
throghout all stages

## Slide 23
Software
Sensor capabilities
Conventional 4-20mA
Fixed ranges, calibrated. Hard limits
Field bus device
The sensor is CAPABLE of measuring from -20 to 200ºC. We can choose any range within that.
If the temperature goes outside the select range, the device keeps measuring normally (maybe with a warning of “outside expected range)
4 mA = 0 ºC
20 mA = 100 ºC

## Slide 24
Software
Importance of dynamic scaling
Up to 150 Kg max
300 Kg pig
This plant is actualy
8 stores high …
2 days after startup

## Slide 25
Software – Comparing with reality

## Slide 26
Software – Comparing with reality

## Slide 27
Software – Birds eye view of ff devices
NoW

## Slide 28
Hacking with a FF device
Thinking outside the conventional
An analyzer is expensive. A small mass flowmeter is a lot less expensive …
Mass Flowmeter

## Slide 29
3 – Remote internet access to a smart FIELD device
ET PHONE HOME - NO
But Home can call ET, as long as we
are listening in on the call.

## Slide 30
Remote Acess
No need to send device to manufacter
DCS Server
DCS CPU
Field
Office Laptop
Share screen
Security certificate
User & Login
Security Firewall
Enable user

## Slide 31
Remote Access
Remote access to auxiliar systems
Auxiliar System
PC
Security certificate
User & Login
Security Firewall
Enable user
German Company
Activate/deactivate
Gateway function at
the Firewall for this ET

## Slide 32
Questions ?

## Slide 33
THANKS